## PK-2260
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-2270
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-2375
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-2660
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-3270
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5270
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5365
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5370
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5465
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5670
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5780
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5791
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-5875
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6280
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6355
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6360
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6365
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6375
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6465
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6660
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6670
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6767
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6781
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-6865
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7270
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7360
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7365
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7375
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7380
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7390
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7670
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7680
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7690
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes

## PK-7875
laboratory_name | PK-2260 |  | Laboratory Ventilation Assesment - Energy Simulation
avg_sash_height | 0 |  | UQAM - Pavillion President Kennedy
ceil_height | 8.4
surface_area | 703 | Simulation Inputs
additional_evac | 272 | Lab Name | PK-2260 | Num. Hoods A | 1 | Night ACH start | 20:00
additional_equipment_max | 0 | Surface Area (sqft) | 703 | Hood Model A | VAV-48-770-175 | Night Occ ACH | 6
additional_equipment_min | 0 | Ceiling Height (ft) | 8.4 | Num. Hoods B | 0 | Night Unoc ACH | 6
num_hoods_a | 1 | Evac Offset (cfm | 272 | Hood Model B | NA | Night Occ Start | 20:00
hood_model_a | VAV-48-770-175 | Equip. Evac Max (cfm) | 0 | Day ACH start | 8:00 | Night Occ Rate | 37.39%
num_hoods_b | 0 | Equip. Evac Min (cfm) | 0 | Day Occ ACH | 6 | Wkd Day Occ Start | 10:00
hood_model_b | NA | Cost of CFM | 5 | Day Unoc ACH | 6 | Wkd Day Occ Rate | 30.38%
day_occupancy_rate | 0.8962 | Sash Height | 0% | Day Occ Start | 8:00 | Wkd Night Occ Start | 18:00
night_occupancy_rate | 0.37391 | Hood Use Rate | 70.62% | Day Occ Rate | 89.62% | Wkd Night Occ Rate | 22.74%
weekend_day_occupancy_rate | 0.3038
weekend_night_occupancy_rate | 0.22745 | Simulations Results
fumehood_occupancy_rate | 0.70616 | description | base lab cfm | equipment inc cfm | sash driven cfm | lab total cfm | savings cfm
day_occupied_ach | 6 | current operation | 862.52 | 0 | 0 | 862.52 | 0
day_unoccupied_ach | 6 | reduced unoccupied ach | 795.7666 | 0 | 0 | 795.7666 | 66.7534
night_occupied_ach | 6 | reduced unoccupied face velocity | 862.52 | 0 | 0 | 862.52 | 0
night_unoccupied_ach | 6 | sash reduced 20% | 862.52 | 0 | 0 | 862.52 | 0
ach_day_start | 8:00 | sash reduced 50% | 862.52 | 0 | 0 | 862.52 | 0
ach_night_start | 20:00 | reduced ach, sash reduced 20% | 798.5971 | 0 | 0 | 798.5971 | 63.9229
cost_cfm | 5 | reduced ach, sash reduced 50% | 798.0074 | 0 | 0 | 798.0074 | 64.5126
day_occupancy_start | 8:00 | all reduced (ach, face vel, sash 50%) | 799.1868 | 0 | 0 | 799.1868 | 63.3332
night_occupancy_start | 20:00
weekend_day_occupancy_start | 10:00
weekend_night_occupancy_start | 18:00
notes
Notes