## Sheet1
Laboratory Ventilation Assesment - Energy Simulation
|  | McGill University |  |  | Page No. | 1
Simulation Inputs
General Information |  |  |  | Lab Parameters
Building | Otto Maass |  |  | Lab size (sqft) |  | 10000
Room No. | 200 |  |  | Ceiling height (ft) |  | 8.75
Occupant | Dr. Lee |  |  | Min ACH - occupied |  | 10
|  |  |  | Min ACH - unocc. |  | 4
Hood Information |  | Type 1 | Type 2 | Evac. for neg pres (cfm) |  | 200
Width (inches) |  | 48 | 72 | Num. of hoods of type 1 |  | 10
Depth (inches) |  | 24 | 24 | Num. of hoods of type 2 |  | 2
Max sash height (inches) |  | 28 | 28 | Cost of a CFM ($/yr) |  | 5.25
Max evac possible (cfm) |  | 800 | 1200 | Lab occupancy start time |  | 8:00
Min evac possible (cfm) |  | 200 | 300 | Lab occupancy end time |  | 22:00
Face vel. - occupied (fpm) |  | 100 | 100 | Hood occupied (%) |  | 50%
Face vel. - unocc. (fpm) |  | 60 | 60 | Sash height (via inspec.) |  | 25%
Simulations Results
Scenario |  |  | Evacuation
No. | Description |  | Base | Hood-driven | Total | Savings
1 | Current opertation |  | 8000 | 2000 | 10000 | 0
2 | Sash height reduc. - 25% |  | 8000 | 1000 | 9000 | 1000
3 | Sash height reduc. - 50% |  | 8000 | 0 | 8000 | 2000
4 | ACH reduction (6 ACH) |  | 6000 | 2000 | 8000 | 2000
5 | Face vel. reduc. (60 fpm) |  | 8000 | 1000 | 9000 | 1000
6 | Combo A: 3 & 4 |  | 6000 | 500 | 6500 | 3500
7 | Combo B: 2, 3 & 4 |  | 6000 | 0 | 6000 | 4000
Notes & Recommendations |  |  | Results Chart